## Calculo CFM
Piso | BLOQUE | Area | altura | volumen | No. Personas | Movimiento Aire |  | A. exterior |  |  | Retorno | Extraccion | Presion | Categoria | Tipo zona | Carga termica |  | Suministro | Retorno | Extraccion
|  | m2 | m | m3 |  | ach | cfm | ach | cfm | % | cfm | cfm |  |  |  | BTU/h | TR
Piso 1 | Bloque #1
| Equipo de Angiografia | 34 | 2.5 | 85 |  | 12 | 601 | [5 empty] | Negative | Health-care | All rooms |  |  | 601
| Imágenes | 15 | 2.5 | 37.5 |  | 10 | 221 | [5 empty] | Negative | Health-care | All rooms
| Sala contraste y preparacion | 16.6 | 2.5 | 41.5 |  | 4 | 98 | [5 empty] | N/R | Health-care | Patient room
| Recuperacion | 31 | 2.5 | 77.5 |  | 12 | 548 | [5 empty] | Negative | Health-care | All rooms
| Pasillo | 33 | 2.5 | 82.5 |  | 2 | 98 | [6 empty] | Health-care | Corridor
| Sala rayos x 1 | 19.3 | 2.5 | 48.25 |  | 12 | 341 | [5 empty] | Negative | Health-care | All rooms
| Control | 9.2 | 2.5 | 23 | 2 |  | 0 |  | 16 | [5 empty] | Oficce Space
| Digitalizacon | 9.4 | 2.5 | 23.5 | 2 |  | 0 |  | 17 | [5 empty] | Oficce Space
| Vestidores | 9.4 | 2.5 | 23.5 | 4 |  | 0 |  | 27 | [5 empty] | Oficce Space
| Sala rayos x 2 | 20 | 2.5 | 50 |  | 12 | 354 | [5 empty] | Negative | Health-care | All rooms
| Control | 9.2 | 2.5 | 23 |  |  | 0 | [7 empty] | Oficce Space
| Digitalizacon | 9.4 | 2.5 | 23.5 |  |  | 0 | [7 empty] | Oficce Space
| Vestidores | 9.4 | 2.5 | 23.5 |  |  | 0
| Ecografia 1 | 18 | 2.5 | 45 |  | 12 | 318 | [5 empty] | Negative | Health-care | All rooms
| Ecografia 2 | 18.3 | 2.5 | 45.75 |  | 12 | 324 | [5 empty] | Negative | Health-care | All rooms
| Ecocardiografia | 18.3 | 2.5 | 45.75 |  | 12 | 324 | [5 empty] | Negative | Health-care | All rooms
| Descanso sala | 14.3 | 2.5 | 35.75 | 3 | 4 | 85 | [5 empty] | N/R |  | Resident dining
| Facturacion | 16 | 2.5 | 40 | 3 |  | 0 |  | 26 | [5 empty] | Oficce Space
| Sala de lectura y t | 17.6 | 2.5 | 44 | 4 |  | 0 |  | 32 | [5 empty] | Oficce Space
| Ecografia 3 | 14.2 | 2.5 | 35.5 |  | 12 | 251 | [5 empty] | Negative | Health-care | All rooms
| Cafetim | 9.4 | 2.5 | 23.5 | 3 |  | 0 |  | 22 | [5 empty] | Oficce Space
| Vestier presonal 1 | 6.4 | 2.5 | 16 |  |  | 0
| Vestier presonal 2 | 6.4 | 2.5 | 16 |  |  | 0
| Coordinación | 10 | 2.5 | 25 | 3 |  | 0 |  | 22 | [5 empty] | Oficce Space
| Cuarto tecnico | 16 | 2.5 | 40 |  |  | 0
| Control de imágenes | 14.5 | 2.5 | 36.25 |  | 10 | 214 | [5 empty] | Negative | Health-care | All rooms
| Equipo de tomografia | 22 | 2.5 | 55 |  | 10 | 324 | [5 empty] | Negative | Health-care | All rooms
| Sala de contraste | 14 | 2.5 | 35 |  | 10 | 207 | [5 empty] | Negative | Health-care | All rooms
| Equipos | 14 | 2.5 | 35
| Sala de resonancia MAG | 25 | 2.5 | 62.5 |  | 12 | 442 | [5 empty] | Negative | Health-care | All rooms
| Deposito Contraste | 13 | 2.5 | 32.5 |  | 10 | 192 | [5 empty] | Negative | Health-care | All rooms
| Trabajo Limpio | 12 | 2.5 | 30 |  | 12 | 212 | [5 empty] | Negative | Health-care | All rooms
| Control Imágenes | 11.7 | 2.5 | 29.25 |  | 10 | 173 | [5 empty] | Negative |  | All rooms
| Area entrevista | 10.6 | 2.5 | 26.5 | 2 |  | 0 |  | 17 | [5 empty] | Oficce Space
| Area de preparacion | 19.3 | 2.5 | 48.25 |  | 4 | 114 | [6 empty] | Health-care | Patient room
| Consultorio 1 | 12.6 | 2.5 | 31.5 |  | 12 | 223 | [5 empty] | Negative | Health-care | All rooms
| Consultorio 2 | 13 | 2.5 | 32.5 |  | 12 | 230 | [5 empty] | Negative | Health-care | All rooms
| Corredor | 195 | 2.5 | 487.5 |  | 2 | 574 | [5 empty] | N/R |  | Corridor
Piso 1 | Bloque #2
| UC intermedio Pediatrico | 308 | 2.5 | 770 |  | 6 | 2720 | [5 empty] | Negative |  | Emergency departament
| Ropa sucia | 10.1 | 2.5 | 25.25 |  | 12 | 179 | [5 empty] | Negative |  | All rooms
| Trabajo sucio | 10.5 | 2.5 | 26.25 |  | 12 | 186 | [5 empty] | Negative |  | All rooms
| RX potatil | 5.5 | 2.5 | 13.75 |  | 6 | 49 | [5 empty] | Negative |  | All rooms
| Trabajo Limpio | 9.2 | 2.5 | 23 |  | 12 | 163 | [5 empty] | Negative |  | All rooms
| Medicamentos | 9.1 | 2.5 | 22.75 |  | 12 | 161 | [5 empty] | Negative |  | All rooms
| Ropa limpia | 8.9 | 2.5 | 22.25 |  | 12 | 158 | [5 empty] | Negative |  | All rooms
| Equipos | 8.7 | 2.5 | 21.75
| Codinacion UCI | 11.5 | 2.5 | 28.75 | 3 |  |  |  | 23 | [5 empty] | Oficce Space
| Locutorio | 14 | 2.5 | 35 | 4 |  |  |  | 30 | [5 empty] | Oficce Space
| Recpcion | 33 | 2.5 | 82.5 | 30 |  |  |  | 172 | [5 empty] | Reception areas
| Descanso Medico | 10.7 | 2.5 | 26.75 |  | 4 | 63 | [5 empty] | N/R |  | Resident dining
| Descanso Pesonal | 10 | 2.5 | 25 |  | 4 | 59 | [5 empty] | N/R |  | Resident dining
| Reepcion e inofrmacion | 33.3 | 2.5 | 83.25 |  |  |  |  | 22 |  |  |  | N/R |  | Reception areas
| Cuarto electrico | 13.4 | 2.5 | 33.5
| Descanso medico | 11 | 2.5 | 27.5 |  | 4 | 65 | [5 empty] | N/R |  | Resident dining
| Descanso personal | 10.2 | 2.5 | 25.5 |  | 4 | 61 | [5 empty] | N/R |  | Resident dining
| Locutorio | 14.1 | 2.5 | 35.25 | 4 |  | 0 |  | 30 | [5 empty] | Oficce Space
| coordinación uci | 11.6 | 2.5 | 29 | 30 |  | 0 |  | 158 | [5 empty] | Oficce Space
| Ropa Sucia | 10.1 | 2.5 | 25.25 |  | 12 | 179 | [5 empty] | Negative |  | All rooms
| Trabajo sucio | 10.5 | 2.5 | 26.25 |  | 12 | 186 | [5 empty] | Negative |  | All rooms
| RX potatil | 5.6 | 2.5 | 14 |  | 12 | 99 | [5 empty] | Negative |  | All rooms
| Trabajo Limpio | 9.2 | 2.5 | 23 |  | 12 | 163 | [5 empty] | Negative |  | All rooms
| Medicamentos | 9.1 | 2.5 | 22.75 |  | 12 | 161 | [5 empty] | Negative |  | All rooms
| Ropa limpia | 9 | 2.5 | 22.5 |  | 12 | 159 | [5 empty] | Negative |  | All rooms
| Equipos | 8.7 | 2.5 | 21.75
| UCI NEONATAL | 496 | 2.5 | 1240 |  | 6 | 4380 | [5 empty] | Negative |  | Emergency departament
Piso 1 | Bloque #3
| Audimetria | 16 | 2.5 | 40 |  | 12 | 283 | [5 empty] | Negative |  | All rooms
| Terapia ocupaional | 26.2 | 2.5 | 65.5 |  | 12 | 463 | [5 empty] | Negative |  | All rooms
| Sala de Hidroterapia | 14.5 | 2.5 | 36.25 |  | 12 | 257 | [5 empty] | Negative |  | All rooms
| Deposito GYM | 12 | 2.5 | 30 |  | 12 | 212 | [5 empty] | Negative |  | All rooms
| Area de Terapias | 22 | 2.5 | 55 |  | 12 | 389 | [5 empty] | Negative |  | All rooms
| Terapia de Lenguaje 1 | 17 | 2.5 | 42.5 |  | 6 | 151 | [5 empty] | Negative |  | All rooms
| Terapia de Lenguaje 2 | 15.2 | 2.5 | 38 |  | 6 | 135 | [5 empty] | Negative |  | All rooms
| Terapia de Lenguaje 3 | 15.2 | 2.5 | 38 |  | 6 | 135 | [5 empty] | Negative |  | All rooms
| Terapia de Lenguaje 4 | 15.2 | 2.5 | 38 |  | 6 | 135 | [5 empty] | Negative |  | All rooms
| Area de GYM | 28.4 | 2.5 | 71 |  | 12 | 502 | [5 empty] | Negative |  | All rooms
| Cuarto de Informacion | 12.2 | 2.5 | 30.5 | 5 |  |  |  | 33 |  |  |  | N/R |  | Reception areas
| Sala de espera | 42 | 2.5 | 105 | 10 |  |  |  | 78 |  |  |  | N/R |  | Reception areas
| Deposito | 20 | 2.5 | 50 |  | 10 | 295 | [5 empty] | Negative |  | All rooms
| Paquetes Calientes | 5.5 | 2.5 | 13.75 |  | 12 | 98 | [5 empty] | Negative |  | All rooms
| Paquetes Frios | 7 | 2.5 | 17.5 |  | 12 | 124 | [5 empty] | Negative |  | All rooms
| Pasillo | 143 | 2.5 | 357.5 |  | 2 | 421
Piso 2 | Bloque #1 |  |  |  |  | ,
| Sala de Cirujia 1 | 22.5 | 2.8 | 63 |  | 25 | 928 | [5 empty] | Positive |  | Operating Room |  |  | 950 |  | 930
| Sala de Cirujia 2 | 22.5 | 2.8 | 63 |  | 25 | 928 | [5 empty] | Positive |  | Operating Room |  |  | 950 |  | 930
| Sala de Cirujia 3 | 22.5 | 2.8 | 63 |  | 25 | 928 | [5 empty] | Positive |  | Operating Room |  |  | 950 |  | 930
| Trabajo Limpio | 9.1 | 2.5 | 22.75 |  | 12 | 161 | [5 empty] | Positive |  | All rooms |  |  | 160
| Deposito de Materiales | 6 | 2.5 | 15 |  | 12 | 106 | [5 empty] | Positive |  | All rooms |  |  | 110
| Descanso Medico | 12.4 | 2.5 | 31 |  | 4 | 73 | [5 empty] | N/R |  | Resident dining |  |  | 100
| Ropa Limpia | 5 | 2.5 | 12.5 |  | 12 | 89 | [5 empty] | Positive |  | All rooms |  |  | 90
| Medicamentos | 9.3 | 2.5 | 23.25 |  | 12 | 165 | [5 empty] | Positive |  | All rooms |  |  | 160
| Equipos | 11.5 | 2.5 | 28.75 |  | 12 | 204 | [5 empty] | Negative |  | All rooms |  |  |  |  | 210
| Deposito de Anestesia | 5 | 2.5 | 12.5 |  | 12 | 89 | [5 empty] | Negative |  | All rooms |  |  |  |  | 100
| Descanso Personal | 11 | 2.5 | 27.5 |  | 4 | 65 | [5 empty] | N/R |  | Resident dining |  |  |  |  | 100
| Sala de recuperacion | 55 | 2.5 | 137.5 |  | 6 | 486 | [5 empty] | Negative |  | All rooms |  |  | 480 |  | 160
| Trabajo Sucio | 6.2 | 2.5 | 15.5 |  | 12 | 110 | [5 empty] | Negative |  | All rooms |  |  |  |  | 150
| Trabajo Limpio | 6.5 | 2.5 | 16.25 |  | 12 | 115 | [5 empty] | Positive |  | All rooms |  |  | 150
| corredor | 77.6 | 2.5 | 194 |  | 2 | 229 | [10 empty] | 630
Piso 2 | Bloque #2
| UCI intermedio Adultos | 308 | 2.5 | 770 |  | 6 | 2720 | [5 empty] | Negative |  | Emergency departament
| Ropa sucia | 10.1 | 2.5 | 25.25 |  | 12 | 179 | [5 empty] | Negative |  | All rooms
| Trabajo sucio | 10.5 | 2.5 | 26.25 |  | 12 | 186 | [5 empty] | Negative |  | All rooms
| RX potatil | 5.5 | 2.5 | 13.75 |  | 12 | 98 | [5 empty] | Negative |  | All rooms
| Trabajo Limpio | 9.2 | 2.5 | 23 |  | 12 | 163 | [5 empty] | Negative |  | All rooms
| Medicamentos | 9.1 | 2.5 | 22.75 |  | 12 | 161 | [5 empty] | Negative |  | All rooms
| Ropa limpia | 9 | 2.5 | 22.5 |  | 12 | 159 | [5 empty] | Negative |  | All rooms
| Equipos | 8.7 | 2.5 | 21.75 |  | 12 | 154 | [5 empty] | Negative |  | All rooms
| Codinacion UCI | 11.5 | 2.5 | 28.75 | 3 |  |  |  | 23 | [5 empty] | Oficce Space
| Locutorio | 14.1 | 2.5 | 35.25 | 10 |  |  |  | 60 | [5 empty] | Oficce Space
| Recpcion | 33 | 2.5 | 82.5 | [8 empty] | N/R |  | Reception areas
| Descanso Medico | 10.8 | 2.5 | 27 |  | 4 | 64 | [5 empty] | N/R |  | Resident dining
| Descanso Pesonal | 10 | 2.5 | 25 |  | 4 | 59 | [5 empty] | N/R |  | Resident dining
| Reepcion e inofrmacion | 37.5 | 2.5 | 93.75 | 10 |  |  |  | 75 |  |  |  | N/R |  | Reception areas
| Cuarto electrico | 13.4 | 2.5 | 33.5
| Descanso medico | 10.8 | 2.5 | 27 |  | 4 | 64 | [5 empty] | N/R |  | Resident dining
| Descanso personal | 10 | 2.5 | 25 |  | 4 | 59 | [5 empty] | N/R |  | Resident dining
| Locutorio | 14.1 | 2.5 | 35.25 | 10 |  |  |  | 60 | [5 empty] | Oficce Space
| coordinación uci | 11.6 | 2.5 | 29 | 3 |  |  |  | 23 | [5 empty] | Oficce Space
| Ropa Sucia | 10.1 | 2.5 | 25.25 |  | 12 | 179 | [5 empty] | Negative |  | All rooms
| Trabajo sucio | 10.5 | 2.5 | 26.25 |  | 12 | 186 | [5 empty] | Negative |  | All rooms
| RX potatil | 5.6 | 2.5 | 14 |  | 12 | 99 | [5 empty] | Negative |  | All rooms
| Trabajo Limpio | 9.2 | 2.5 | 23 |  | 12 | 163 | [5 empty] | Negative |  | All rooms
| Medicamentos | 9.1 | 2.5 | 22.75 |  | 12 | 161 | [5 empty] | Negative |  | All rooms
| Ropa limpia | 9 | 2.5 | 22.5 |  | 12 | 159 | [5 empty] | Negative |  | All rooms
| Equipos | 8.7 | 2.5 | 21.75 |  | 12 | 154 | [5 empty] | Negative |  | All rooms
| UCI Adultos | 552 | 2.5 | 1380 |  | 6 | 4875 | [5 empty] | Negative |  | Emergency departament
Piso 2 | Bloque #3
| Auditoriio | 36 | 2.5 | 90 | 35 | 4 | 212 |  | 199 | [5 empty] | Auditorium Seating area
| Aula 1 | 24.7 | 2.5 | 61.75 | 15 | 6 | 219 |  | 107 | [5 empty] | Classrooms
| Aula 2 | 24.7 | 2.5 | 61.75 | 15 | 4 | 146 |  | 107 | [5 empty] | Classrooms
| Aula 3 | 24.7 | 2.5 | 61.75 | 15 | 4 | 146 |  | 107 | [5 empty] | Classrooms
| Habitaciones 1 | 24.7 | 2.5 | 61.75 |  | 4 | 146 | [7 empty] | Patient room
| Habitaciones 2 | 23.6 | 2.5 | 59 |  | 4 | 139 | [7 empty] | Patient room
| Habitaciones 3 | 30.2 | 2.5 | 75.5 |  | 4 | 178 | [7 empty] | Patient room
| Biblioteca | 57 | 2.5 | 142.5 | 10 |  |  |  | 87 | [5 empty] | Office space
| Bienestar Universitario | 52 | 2.5 | 130 | 15 |  |  |  | 109 | [5 empty] | Office space
| Area Multiple 1 | 24 | 2.5 | 60 | 4 |  |  |  | 52 | [5 empty] | Classrooms
| Area Multiple 2 | 24 | 2.5 | 60 | 4 |  |  |  | 52 | [5 empty] | Classrooms
| Area Multiple 3 | 24 | 2.5 | 60 | 15 |  |  |  | 107 | [5 empty] | Classrooms
| Coordinación | 18.3 | 2.5 | 45.75 | 15 |  |  |  | 99 | [5 empty] | Classrooms
| Recpcion | 40.6 | 2.5 | 101.5 | 8 |  |  |  | 67 | [5 empty] | Office space
Piso 3 | Bloque #2
| Habitacion 1 | 18.6 | 2.5 | 46.5 |  | 4 | 110 | [6 empty] | N/R | Patient room
| Habitacion 2 | 17.7 | 2.5 | 44.25 |  | 4 | 105 | [6 empty] | N/R | Patient room
| Habitacion 3 | 17.3 | 2.5 | 43.25 |  | 4 | 102 | [6 empty] | N/R | Patient room
| Habitacion 4 | 15 | 2.5 | 37.5 |  | 4 | 89 | [6 empty] | N/R | Patient room
| Habitacion 5 | 15 | 2.5 | 37.5 |  | 4 | 89 | [6 empty] | N/R | Patient room
| Habitacion 6 | 17.3 | 2.5 | 43.25 |  | 4 | 102 | [6 empty] | N/R | Patient room
| Habitacion 7 | 17 | 2.5 | 42.5 |  | 4 | 101 | [6 empty] | N/R | Patient room
| Habitacion 8 | 14.2 | 2.5 | 35.5 |  | 4 | 84 | [6 empty] | N/R | Patient room
| Habitacion 9 | 15.1 | 2.5 | 37.75 |  | 4 | 89 | [6 empty] | N/R | Patient room
| Sala de obsevacion | 14 | 2.5 | 35 |  | 4 | 83 | [6 empty] | N/R | Patient room
| Habitacion 10 | 13.4 | 2.5 | 33.5 |  | 4 | 79 | [6 empty] | N/R | Patient room
| Habitacion 11 | 14.3 | 2.5 | 35.75 |  | 4 | 85 | [6 empty] | N/R | Patient room
| Oficina | 14 | 2.5 | 35 | 3 |  |  |  | 25 | [5 empty] | Oficce Space
| Recepcion e informacion | 43.6 | 2.5 | 109 | 15 |  |  |  | 104 |  |  |  |  | N/R | Reception areas
| Habitacion 12 | 16.8 | 2.5 | 42 |  | 4 | 99 | [6 empty] | N/R | Patient room
| Habitacion 13 | 16.8 | 2.5 | 42 |  | 4 | 99 | [6 empty] | N/R | Patient room
| Habitacion 14 | 15 | 2.5 | 37.5 |  | 4 | 89 | [6 empty] | N/R | Patient room
| Habitacion 15 | 15 | 2.5 | 37.5 |  | 4 | 89 | [6 empty] | N/R | Patient room
| Habitacion 16 | 16.8 | 2.5 | 42 |  | 4 | 99 | [6 empty] | N/R | Patient room
| Habitacion 17 | 16.8 | 2.5 | 42 |  | 4 | 99 | [6 empty] | N/R | Patient room
| Habitacion 18 | 16.8 | 2.5 | 42 |  | 4 | 99 | [6 empty] | N/R | Patient room
| Habitacion 19 | 15 | 2.5 | 37.5 |  | 4 | 89 | [6 empty] | N/R | Patient room
| Habitacion 20 | 15 | 2.5 | 37.5 |  | 4 | 89 | [6 empty] | N/R | Patient room
| Habitacion 21 | 16.8 | 2.5 | 42 |  | 4 | 99 | [6 empty] | N/R | Patient room
| Habitacion 22 | 16.8 | 2.5 | 42 |  | 4 | 99 | [6 empty] | N/R | Patient room
| Habitacion 23 | 13.4 | 2.5 | 33.5 |  | 4 | 79 | [6 empty] | N/R | Patient room
| Habitacion 24 | 13.5 | 2.5 | 33.75 |  | 4 | 80 | [6 empty] | N/R | Patient room
| Habitacion 25 | 13.4 | 2.5 | 33.5 |  | 4 | 79 | [6 empty] | N/R | Patient room
| Habitacion 26 | 15.3 | 2.5 | 38.25 |  | 4 | 91 | [6 empty] | N/R | Patient room
| Sala de obsevacion | 12 | 2.5 | 30 |  | 4 | 71 | [6 empty] | N/R | Patient room
| Habitacion 27 | 13.3 | 2.5 | 33.25 |  | 4 | 79 | [6 empty] | N/R | Patient room
| Habitacion 28 | 14.4 | 2.5 | 36 |  | 4 | 85 | [6 empty] | N/R | Patient room
Piso 3 | Bloque #3
| Auditorio | 32.8 | 2.5 | 82 | 100 | 6 | 290 |  | 522 | [5 empty] | Auditorium Seating area
| Central de Sistemas | 36.6 | 2.5 | 91.5 | 20 |  | 0 |  | 124 | [5 empty] | Telephone
| Atencion telefonica y Virtual | 24.6 | 2.5 | 61.5 | 6 |  | 0 |  | 46 | [5 empty] | Telephone
| Deposito de Material | 25 | 2.5 | 62.5 |  | 4 | 148 |  | 33 | [5 empty] | Classrooms
| Habitacion personal | 23.5 | 2.5 | 58.75 |  | 4 | 139 | [7 empty] | Patient room
| GYM | 30 | 2.5 | 75 |  | 12 | 530 | [7 empty] | all room
| Referencia y Contrareferncia | 155 | 2.5 | 387.5 | 20 | 6 | 1369 |  | 201 | [5 empty] | Oficce Space
| Area de Atencion y prevenvion | 52 | 2.5 | 130 |  | 6 | 460 |  | 34 | [5 empty] | Oficce Space
| Capacitacion 1 | 23.8 | 2.5 | 59.5 |  | 6 | 211 |  | 31 | [5 empty] | Classrooms
| Capacitacion 2 | 23.8 | 2.5 | 59.5 |  | 6 | 211 |  | 31 | [5 empty] | Classrooms
| Coordinación | 23.8 | 2.5 | 59.5 | 4 | 5 | 176 |  | 36 | [5 empty] | Oficce Space
| Recepcion | 31.7 | 2.5 | 79.25 | 15 | 6 | 280 |  | 96 | [5 empty] | Reception areas
[21 empty] | Ubicación |  |  | Suministro | Retorno | Extraccion | Suministro | Retorno | Extraccion
[21 empty] | SOTANO | Servicios generales medicos
[23 empty] | Entrega cadaveres | 160 |  | 200 | 160 |  | 200
[23 empty] | Entrega cadaveres | 160 |  | 200 | 160 |  | 200
[23 empty] | Residuos raros |  |  | 100 |  |  | 100
[23 empty] | Autopsias | 240 |  | 300 | 240 |  | 300
[23 empty] | Deposito cadaveres | [5 empty] | 150
[23 empty] | Pasillo morgue | 160 |  | 160 | 80
[22 empty] | Otros | Cuarto gases |  |  | 320 |  |  | 320
[23 empty] | Cuarto vacio | 150 |  | 150 | 150 |  | 150
Rack comunicaciones

## Hoja1
Ubicación | area | altura | volumen | No. Personas | suminstro |  | A. exterior |  |  | Retorno | Extraccion | Presion | Categoria | Tipo zona | Carga termica |  | Categoria | Tipo zona | A.ext |  |  | suministro | Presion | Recirculacion
| m2 | m | m3 |  | ach | cfm | ach | cfm | % | cfm | cfm |  |  |  | CFM | TR |  |  | cfm/pers | cfm/ft2 | ach | ach
Hospitalizacion | [16 empty] | Dormitories | Bedroom | 5 | 0.06
Control, informacion y caja | 11.5 | 3 | 34.5 |  |  |  |  | 8 |  |  |  | n/a | Office buildings | Reception areas |  | 0 | Dormitories | Living room | 5 | 0.06
Sala EDA | 11.3 | 3 | 33.9 |  | 6 | 120 | 2 | 40 | 33.33% | 80 |  | n/a | Health-care | Examination room |  | 0 | Education facilities | Classroom | 10 | 0.12
Reanimacion | 14.3 | 3 | 42.9 |  | 15 | 379 | 3 | 76 | 20.05% | 303 |  | positiva | Health-care | Trauma room |  | 0 | Health-care | Clean workroom |  |  | 2 | 4 | positiva
Oficina Radio | 4.6 | 3 | 13.8 |  |  |  |  | 3 |  |  |  | n/a | Office buildings | Office space |  | 0 | Health-care | Corridor |  |  |  | 2 | n/a
Sala ERA | 15.2 | 3 | 45.6 |  | 6 | 162 | 2 | 54 | 33.33% | 108 |  | n/a | Health-care | Examination room |  | 0 | Health-care | Darkroom |  |  | 2 | 10 | negativa | No
Pasillo urgencias | 40.1 | 3 | 120.3 |  | 6 | 425 | 2 | 142 | 33.41% | 283 |  | n/a | Health-care | Examination room |  | 0 | Health-care | Examination room |  |  | 2 | 6 | n/a
Curaciones y ferulizaciones | 11 | 3 | 33 |  | 6 | 117 | 2 | 39 | 33.33% | 78 |  | n/a | Health-care | Treatment room |  | 0 | Health-care | Hazardous material |  |  | 2 | 10 | negativa | No
Observacion urgencias | 129.3 | 3 | 387.9 |  | 6 | 1371 | 2 | 457 | 33.33% | 914 |  | n/a | Health-care | Examination room |  | 0 | Health-care | laboratory general |  |  | 2 | 6 | n/a
T. limpio | 3.1 | 3 | 9.3 |  | 4 | 22 | 2 | 11 | 50% | 11 |  | positiva | Health-care | Clean workroom |  | 0 | Health-care | Newborn intensive care |  |  | 2 | 6 | positiva
Equipos | 2.5 | 3 | 7.5 |  |  |  |  | 0 |  |  |  | n/a | Miscellaneous spaces | Warehouses |  | 0 | Health-care | Newborn nursery |  |  | 2 | 6 | n/a
Espera interna y pasillo | 40 | 3 | 120 |  | 2 | 142 | 0 | 0 | 0% | 142 |  | n/a | Health-care | Corridor |  | 0 | Health-care | Patient room |  |  | 2 | 6 | n/a
T. Sucio | 1.6 | 3 | 4.8 |  | 6 | 17 | 2 | 6 | 35.29% |  | 17 | negativa | Health-care | Soiled room |  | 0 | Health-care | Pharmacy |  |  | 2 | 4 | positiva
Consultoria Triage | 12.9 | 3 | 38.7 |  | 12 | 274 | 2 | 46 | 16.79% |  | 274 | negativa | Health-care | Triage |  | 0 | Health-care | Protective environment |  |  | 2 | 12 | positiva
Consultorio 1 | 12.7 | 3 | 38.1 |  | 6 | 135 | 2 | 45 | 33.33% | 90 |  | n/a | Health-care | Examination room |  | 0 | Health-care | Soiled room |  |  | 2 | 6 | negativa | No
Consultorio 2 | 12.7 | 3 | 38.1 |  | 6 | 135 | 2 | 45 | 33.33% | 90 |  | n/a | Health-care | Examination room |  | 0 | Health-care | Sterile storage |  |  | 2 | 4 | positiva
Sala espera | 43.1 | 3 | 129.3 |  | 2 | 153 | 0 | 0 | 0% | 153 |  | n/a | Health-care | Corridor |  | 0 | Health-care | Trauma room |  |  | 3 | 15 | positiva
Imagenologia | [16 empty] | Health-care | Treatment room |  |  | 2 | 6 | n/a
Oficina radiologo | 6.5 | 3 | 19.5 |  |  |  |  | 5 |  |  |  | n/a | Office buildings | Office space |  | 0 | Health-care | Triage |  |  | 2 | 12 | negativa | No
Ecografia | 15.1 | 3 | 45.3 |  | 6 | 160 | 2 | 54 | 33.75% | 106 |  | n/a | Health-care | Patient room |  | 0 | Health-care | X-ray |  |  | 2 | 6 | n/a
Sala RX | 20 | 3 | 60 |  | 6 | 212 | 2 | 71 | 33.49% | 141 |  | n/a | Health-care | X-ray |  | 0 | Miscellaneous spaces | Warehouses |  | 0.06
Control RX | 6.2 | 3 | 18.6 |  | 6 | 66 | 2 | 22 | 33.33% | 44 |  | n/a | Health-care | X-ray |  | 0 | Office buildings | Office space | 5 | 0.06
Cuarto revelado | 6.8 | 3 | 20.4 |  | 10 | 121 | 2 | 25 | 20.66% |  | 121 | negativa | Health-care | Darkroom |  | 0 | Office buildings | Reception areas | 5 | 0.06
Laboratorio Clinico
Toma muestras ginecologo | 15.4 | 3 | 46.2 |  | 6 | 164 | 2 | 55 | 33.54% | 109 |  | n/a | Health-care | Examination room |  | 0
Oficina coordinador | 8.2 | 3 | 24.6 |  |  |  |  | 6 |  |  |  | n/a | Office buildings | Office space |  | 0
Toma muestras 1 | 5.2 | 3 | 15.6 |  | 6 | 56 | 2 | 19 | 33.93% | 37 |  | n/a | Health-care | Examination room |  | 0
Toma muestras 2 | 5.2 | 3 | 15.6 |  | 6 | 56 | 2 | 19 | 33.93% | 37 |  | n/a | Health-care | Examination room |  | 0
Almacen muestras | 9 | 3 | 27 |  | 10 | 159 | 2 | 32 | 20.13% |  | 159 | negativa | Health-care | Hazardous material |  | 0
Laboratorio especial | 28.8 | 3 | 86.4 |  | 6 | 306 | 2 | 102 | 33.33% | 204 |  | n/a | Health-care | laboratory general |  | 0
Lavado | 3.3 | 3 | 9.9 |  | 4 | 24 | 2 | 12 | 50% | 12 |  | positiva | Health-care | Clean workroom |  | 0
Pasillo laboratorio | 16.4 | 3 | 49.2 |  | 2 | 58 | 0 | 0 | 0% | 58 |  | n/a | Health-care | Corridor |  | 0
Esterilizacion
Esclusa | 2.1 | 3 | 6.3 |  | 12 | 45 | 2 | 8 | 17.78% | 37 |  | positiva | Health-care | Protective environment |  | 0
Entrega y almacen | 9.9 | 3 | 29.7 |  | 12 | 210 | 2 | 35 | 16.67% | 175 |  | positiva | Health-care | Protective environment |  | 0
Clasificacion | 10.5 | 3 | 31.5 |  | 12 | 223 | 2 | 38 | 17.04% | 185 |  | positiva | Health-care | Protective environment |  | 0
Recepcion y lavado | 5.6 | 3 | 16.8 |  | 12 | 119 | 2 | 20 | 16.81% | 99 |  | positiva | Health-care | Protective environment |  | 0
Obstetricia
Atencion a la familia | 8.9 | 3 | 26.7 |  | 6 | 95 | 2 | 32 | 33.68% | 63 |  | n/a | Health-care | Patient room |  | 0
Recuperacion | 19 | 3 | 57 |  | 6 | 202 | 2 | 68 | 33.66% | 134 |  | n/a | Health-care | Newborn nursery |  | 0
Sala de partos | 21.9 | 3 | 65.7 |  | 6 | 233 | 2 | 78 | 33.48% | 155 |  | n/a | Health-care | Newborn nursery |  | 0
Atencion neo-natal | 8.2 | 3 | 24.6 |  | 6 | 87 | 2 | 29 | 33.33% | 58 |  | positiva | Health-care | Newborn intensive care |  | 0
Trabajo de parto 1 | 12.5 | 3 | 37.5 |  | 6 | 133 | 2 | 45 | 33.83% | 88 |  | n/a | Health-care | Newborn nursery |  | 0
Trabajo de parto 2 | 12.5 | 3 | 37.5 |  | 6 | 133 | 2 | 45 | 33.83% | 88 |  | n/a | Health-care | Newborn nursery |  | 0
Acceso filtro | 6.1 | 3 | 18.3 |  | 12 | 130 | 2 | 22 | 16.92% | 108 |  | positiva | Health-care | Protective environment |  | 0
Deposito residuos | 5.6 | 3 | 16.8 |  | 10 | 99 | 2 | 20 | 20.2% |  | 99 | negativa | Health-care | Hazardous material |  | 0
Descanso personal | 6.2 | 3 | 18.6 |  | 2 | 22 | 0 | 0 | 0% | 22 |  | n/a | Health-care | Corridor |  | 0
Prelavado | 4.8 | 3 | 14.4 |  | 4 | 34 | 2 | 17 | 50% | 17 |  | positiva | Health-care | Clean workroom |  | 0
Trabajo sucio | 3.5 | 3 | 10.5 |  | 6 | 38 | 2 | 13 | 34.21% |  | 38 | negativa | Health-care | Soiled room |  | 0
Trabajo limpio | 4.1 | 3 | 12.3 |  | 4 | 29 | 2 | 15 | 51.72% | 14 |  | positiva | Health-care | Clean workroom |  | 0
Recepcion | 5.2 | 3 | 15.6 |  |  |  |  | 4 |  |  |  | n/a | Office buildings | Reception areas |  | 0
Pasillo obstetricia sup. | 32.7 | 3 | 98.1 |  | 2 | 116 | 0 | 0 | 0% | 116 |  | n/a | Health-care | Corridor |  | 0
Pasillo obstetricia inf. | 20.8 | 3 | 62.4 |  | 2 | 74 | 0 | 0 | 0% | 74 |  | n/a | Health-care | Corridor |  | 0
Hospitalizacion
Area esteril | 3.7 | 3 | 11.1 |  | 4 | 27 | 2 | 14 | 51.85% | 13 |  | positiva | Health-care | Sterile storage |  | 0
Area limpia | 5.1 | 3 | 15.3 |  | 4 | 37 | 2 | 19 | 51.35% | 18 |  | positiva | Health-care | Clean workroom |  | 0
Lactancia | 4.8 | 3 | 14.4 |  | 6 | 51 | 2 | 17 | 33.33% | 34 |  | n/a | Health-care | Patient room |  | 0
Trabajo limpio | 4.5 | 3 | 13.5 |  | 4 | 32 | 2 | 16 | 50% | 16 |  | positiva | Health-care | Clean workroom |  | 0
Curaciones | 8.6 | 3 | 25.8 |  | 6 | 92 | 2 | 31 | 33.7% | 61 |  | n/a | Health-care | Treatment room |  | 0
Habitacion | 26.9 | 3 | 80.7 |  | 6 | 286 | 2 | 96 | 33.57% | 190 |  | n/a | Health-care | Patient room |  | 0
Pasillo hospitalizacion | 81.6 | 3 | 244.8 |  | 2 | 289 | 0 | 0 | 0% | 289 |  | n/a | Health-care | Corridor |  | 0
Trabajo sucio | 2.4 | 3 | 7.2 |  | 6 | 26 | 2 | 9 | 34.62% |  | 26 | negativa | Health-care | Soiled room |  | 0
Oficinas
Sala juntas | 17.6 | 3 | 52.8 |  |  |  |  | 12 |  |  |  | n/a | Office buildings | Office space |  | 0
Secretaria y archivo | 9.5 | 3 | 28.5 |  |  |  |  | 7 |  |  |  | n/a | Office buildings | Office space |  | 0
Oficina gerencia | 20.5 | 3 | 61.5 |  |  |  |  | 14 |  |  |  | n/a | Office buildings | Office space |  | 0
Tesoreria | 11.3 | 3 | 33.9 |  |  |  |  | 8 |  |  |  | n/a | Office buildings | Office space |  | 0
Puestos abiertos | 15.4 | 3 | 46.2 |  |  |  |  | 10 |  |  |  | n/a | Office buildings | Office space |  | 0
Of. Subgerente medico | 11.9 | 3 | 35.7 |  |  |  |  | 8 |  |  |  | n/a | Office buildings | Office space |  | 0
Of. Subgerente administrativo | 11.9 | 3 | 35.7 |  |  |  |  | 8 |  |  |  | n/a | Office buildings | Office space |  | 0
Farmacia | 19.9 | 3 | 59.7 |  | 4 | 141 | 2 | 71 | 50.35% | 70 |  | positiva | Health-care | Pharmacy |  | 0
Sala multiple | 50.4 | 3 | 151.2 |  |  |  |  | 33 |  |  |  | n/a | Education facilities | Classroom |  | 0
Archivo | 18.1 | 3 | 54.3 |  |  |  |  | 12 |  |  |  | n/a | Office buildings | Office space |  | 0
Clasificacion | 18.4 | 3 | 55.2 |  |  |  |  | 12 |  |  |  | n/a | Office buildings | Office space |  | 0
Vivienda medica - sala | 17.5 | 3 | 52.5 |  |  |  |  | 0 |  |  |  | n/a | Dormitories | Living room |  | 0
Vivienda medica - Hab.1 | 6.1 | 3 | 18.3 |  |  |  |  | 4 |  |  |  | n/a | Dormitories | Bedroom |  | 0
Vivienda medica - Hab.2 | 9 | 3 | 27 |  |  |  |  | 6 |  |  |  | n/a | Dormitories | Bedroom |  | 0
Consulta externa
Oficina SIAU | 6.1 | 3 | 18.3 |  |  |  |  | 4 |  |  |  | n/a | Office buildings | Office space |  | 0
Oficina coordinacion | 8.1 | 3 | 24.3 |  |  |  |  | 6 |  |  |  | n/a | Office buildings | Office space |  | 0
Facturacion | 5.1 | 3 | 15.3 |  |  |  |  | 4 |  |  |  | n/a | Office buildings | Office space |  | 0
Cons. Servicios medicos 1 | 10.9 | 3 | 32.7 |  | 6 | 116 | 2 | 39 | 33.62% | 77 |  | n/a | Health-care | Examination room |  | 0
Cons. Servicios medicos 2 | 10.9 | 3 | 32.7 |  | 6 | 116 | 2 | 39 | 33.62% | 77 |  | n/a | Health-care | Examination room |  | 0
Cons. PyP 1 | 13.8 | 3 | 41.4 |  | 6 | 147 | 2 | 49 | 33.33% | 98 |  | n/a | Health-care | Examination room |  | 0
Cons. PyP 2 | 13.8 | 3 | 41.4 |  | 6 | 147 | 2 | 49 | 33.33% | 98 |  | n/a | Health-care | Examination room |  | 0
Cons. Vacunacion | 16 | 3 | 48 |  | 6 | 170 | 2 | 57 | 33.53% | 113 |  | n/a | Health-care | Examination room |  | 0
Cons. Enfermeria | 17 | 3 | 51 |  | 6 | 181 | 2 | 61 | 33.7% | 120 |  | n/a | Health-care | Examination room |  | 0
Cons. Medicina esp. | 16.1 | 3 | 48.3 |  | 6 | 171 | 2 | 57 | 33.33% | 114 |  | n/a | Health-care | Examination room |  | 0
Cons. Medicina general 1 | 12 | 3 | 36 |  | 6 | 128 | 2 | 43 | 33.59% | 85 |  | n/a | Health-care | Examination room |  | 0
Cons. Medicina general 2 | 12 | 3 | 36 |  | 6 | 128 | 2 | 43 | 33.59% | 85 |  | n/a | Health-care | Examination room |  | 0
Cons. Medicina general 3 | 12 | 3 | 36 |  | 6 | 128 | 2 | 43 | 33.59% | 85 |  | n/a | Health-care | Examination room |  | 0
Cons. Medicina general 4 | 12 | 3 | 36 |  | 6 | 128 | 2 | 43 | 33.59% | 85 |  | n/a | Health-care | Examination room |  | 0
Cons. Medicina general 5 | 12 | 3 | 36 |  | 6 | 128 | 2 | 43 | 33.59% | 85 |  | n/a | Health-care | Examination room |  | 0
Cons. Apoyo terapeutico | 16 | 3 | 48 |  | 6 | 170 | 2 | 57 | 33.53% | 113 |  | n/a | Health-care | Examination room |  | 0
Cons. Odontologia | 32.8 | 3 | 98.4 |  | 6 | 348 | 2 | 116 | 33.33% | 232 |  | n/a | Health-care | Examination room |  | 0
RX odontologia | 3.5 | 3 | 10.5 |  | 6 | 38 | 2 | 13 | 34.21% | 25 |  | n/a | Health-care | X-ray |  | 0
Esterilizacion odontologia | 2.6 | 3 | 7.8 |  | 12 | 56 | 2 | 10 | 17.86% | 46 |  | positiva | Health-care | Protective environment |  | 0
Circulacion publica
Sala espera consulta externa | 100.2 | 3.5 | 350.7 |  | 2 | 413 | 0 | 0 | 0% | 413 |  | n/a | Health-care | Corridor |  | 0
Sala espera izquierda | 124.7 | 3.5 | 436.45 |  | 2 | 514 | 0 | 0 | 0% | 514 |  | n/a | Health-care | Corridor |  | 0
Sala espera derecha | 129.4 | 3.5 | 452.9 |  | 2 | 534 | 0 | 0 | 0% | 534 |  | n/a | Health-care | Corridor |  | 0
Oratorio | 5.8 | 3.5 | 20.3 |  | 2 | 24 | 0 | 0 | 0% | 24 |  | n/a | Health-care | Corridor |  | 0